## PT-004
| Customer / Client |  |  |  |  | : | Kelington Technologies Sdn.Bhd | [7 empty] | Report No. |  |  | : | CE-21-DPT-KE-JOB6-024
| Project |  |  |  |  | : | Synthomer Job6 Project 2020 | [7 empty] | Date of Test |  |  | : | 2021-01-27
| Location of Test |  |  |  |  | : | Pasir Gudang, Johor
| Test Procedure No. |  |  |  |  | : | CE-PT-01 Rev.1 | [7 empty] | Test Specification |  |  | : | ASME Sec V
| Acceptance Criteria |  |  |  |  | : | ASME B31.3
| Test Method |  |  |  |  | : | Visible | [7 empty] | Test Temperature |  |  | : | Ambient
| Penetrant |  |  |  |  | : | Sherwin Dubl Chek DP 50 | [7 empty] | Light Type |  |  | : | Natural
| Developer |  |  |  |  | : | Sherwin Dubl Chek D 100 | [7 empty] | Dwell Time |  |  | : | 5-15 minutes
| Cleaner |  |  |  |  | : | Sherwin Dubl Chek DR 60 | [7 empty] | Surface Condition |  |  | : | Welded
| Method of Applying Developer | [6 empty] | : | Spraying
| Method of Applying Penetrant | [6 empty] | : |  | Brushing |  | √ | Spraying
No. |  | DESCRIPTION | [8 empty] | Joint No. |  |  | Size (inch) |  |  | SCH |  | Thick. (mm) |  | Material | Results
1 |  | LINE NO.: 30956-3''-150HW06-IM-NI DRAWING NO.: 25150-52-AJ-30956-06 | [8 empty] | 2A |  |  | 3" |  |  | 10S |  | 3.05 |  | SS | ACC
REMARKS :
1. DPT was carried out on the mentioned item above.
2. No significant indication was noticed during inspection.
3. Refer attachment for details
Tested By: | [9 empty] | Reviewed and Approved By: | [8 empty] | Client's Representative:
Name |  |  | : | Max Addelly | [5 empty] | Name | : | [7 empty] | Name | :
Qual |  |  | : | ASNT SF-CE-PT-L2-001 | [5 empty] | Date | : | [7 empty] | Date | :
Date |  |  | : | 2021-01-27
| Customer / Client |  |  |  | : | Kelington Technologies Sdn.Bhd | [8 empty] | Report No. |  |  | : | CE-21-DPT-KE-JOB6-024
| Project / Rig |  |  |  | : | Synthomer Job6 Project 2020 | [8 empty] | Date of Test |  |  | : | 2021-01-27
| Location of Test |  |  |  | : | Pasir Gudang, Johor
Attachment :
| Figure 1: - | [14 empty] | Figure 2: -
| N/A | [14 empty] | N/A
| Figure 3: - | [14 empty] | Figure 4: -
| N/A | [14 empty] | N/A
| Figure 5: - | [14 empty] | Figure 6: -
| N/A | [14 empty] | N/A
Carbon Energy Inspection Sdn Bhd
LIQUID PENETRANT TEST REPORT
Carbon Energy Inspection Sdn Bhd
LIQUID PENETRANT TEST REPORT