## MPT 2
| Customer / Client |  |  |  |  | : | Kelington Technologies Sdn.Bhd |  |  |  |  | Report No. |  |  | : | CE-21-MPT-KE-ROOFRAFTEJT5-042
| Project / Rig |  |  |  |  | : | Synthomer Job6 Project 2020 |  |  |  |  | Date of Test |  |  | : | 2021-02-09
| Location of Test |  |  |  |  | : | Pasir Gudang, Johor
| Test Procedure No. |  |  |  |  | : | CE-MT-01 Rev.2 |  |  |  |  | Test Specification |  |  | : | ASME sec V
| Acceptance Criteria |  |  |  |  | : | ASME B31.3
| Magnetization Unit |  |  |  |  | : | / | AC | DC |  | Permanent
| Yoke Serial No |  |  |  |  | : | 1603044 |  |  |  |  | Pole Spacing |  |  | : | 3 inches to 8 inches
| Flux Indicator |  |  |  |  | : | Chemitall Burma Castrol |  |  |  |  | Lifting Capacity |  |  | : | 40lbs (18.5KG)
| Type Of Inspection |  |  |  |  | : | Wet |  |  |  |  | Contrast Paint |  |  | : | Sherwin White Contrast CP-2
| Light Type |  |  |  |  | : | Natural |  |  |  |  | Magnetic Ink |  |  | : | Sherwin Black Oxide BO-1
| Visible Light Intensity |  |  |  |  | : | 800-1000 lux |  |  |  |  | Method |  |  | : | Black and white
No. |  | DESCRIPTION | [8 empty] | Joint No. | Size (inch) |  | Thick. (mm) |  |  | Material |  | Welding Process | Results
1 |  | ROOF RAFTER JOINT | [8 empty] | JT5-1 | - |  | 12 |  |  | CS |  | SMAW | ACC
2 |  | ROOF RAFTER JOINT | [8 empty] | JT5-2 | - |  | 12 |  |  | CS |  | SMAW | ACC
3 |  | ROOF RAFTER JOINT | [8 empty] | JT5-3 | - |  | 12 |  |  | CS |  | SMAW | ACC
4 |  | ROOF RAFTER JOINT | [8 empty] | JT5-4 | - |  | 12 |  |  | CS |  | SMAW | ACC
5 |  | ROOF RAFTER JOINT | [8 empty] | JT5-5 | - |  | 12 |  |  | CS |  | SMAW | ACC
6 |  | ROOF RAFTER JOINT | [8 empty] | JT5-6 | - |  | 12 |  |  | CS |  | SMAW | ACC
7 |  | ROOF RAFTER JOINT | [8 empty] | JT5-7 | - |  | 12 |  |  | CS |  | SMAW | ACC
8 |  | ROOF RAFTER JOINT | [8 empty] | JT5-8 | - |  | 12 |  |  | CS |  | SMAW | ACC
9 |  | ROOF RAFTER JOINT | [8 empty] | JT5-9 | - |  | 12 |  |  | CS |  | SMAW | ACC
10 |  | ROOF RAFTER JOINT | [8 empty] | JT5-10 | - |  | 12 |  |  | CS |  | SMAW | ACC
11 |  | ROOF RAFTER JOINT | [8 empty] | JT5-11 | - |  | 12 |  |  | CS |  | SMAW | ACC
12 |  | ROOF RAFTER JOINT | [8 empty] | JT5-12 | - |  | 12 |  |  | CS |  | SMAW | ACC
13 |  | ROOF RAFTER JOINT | [8 empty] | JT5-13 | - |  | 12 |  |  | CS |  | SMAW | ACC
REMARKS :
1. MPT was carried out on the mantioned item above.
2. No significant indication was noticed during inspection.
3. Refer attachment for details
Tested By: | [8 empty] | Reviewed and Approved By: | [6 empty] | Client's Representative:
Name |  |  | : | RODOLFO TINDIK |  |  |  |  | Name | : | [5 empty] | Name |  | :
Qual |  |  | : | ASNT LEVEL II |  |  |  |  | Date | : | [5 empty] | Date |  | :
Date |  |  | : | 2021-01-20
| Customer / Client |  |  |  | : | Kelington Technologies Sdn.Bhd | [5 empty] | Report No. |  |  | : | CE-21-MPT-KE-ROOFRAFTEJT5-042
| Project / Rig |  |  |  | : | Synthomer Job6 Project 2020 | [5 empty] | Date of Test |  |  | : | 2021-02-09
| Location of Test |  |  |  | : | Pasir Gudang, Johor
Attachment :
| Figure 1: - JN 1 | [11 empty] | Figure 2: - JN 1
| N/A | [11 empty] | N/A
| Figure 3: | [11 empty] | Figure 4: -
| N/A | [11 empty] | N/A
| Figure 5: - | [11 empty] | Figure 6: -
| N/A | [11 empty] | N/A
Carbon Energy Inspection Sdn Bhd
MAGNETIC PARTICLE TEST REPORT
Carbon Energy Inspection Sdn Bhd
MAGNETIC PARTICLE TEST REPORT